## Slide 1: BASIC PRINCIPLES IN OCCUPATIONAL HYGIENE
Day 2

## Slide 2: 10 - VENTILATION

## Slide 3: GENERAL VENTILATION

## Slide 4
Local exhaust ventilation (LEV) systems
Source: Adrian Hirst
Notes: <number>
Photo showing typical components in a real LEV system

## Slide 5: General Features of an LEV System
Source: Adrian Hirst

## Slide 6: General Considerations
Source: HSE

## Slide 7: Inlets/Hoods

## Slide 8
Local exhaust ventilation hoods:
Capture mobile
Source: HSE
Notes: <number>
There are a large range of different types and designs of LEV hood and there appears to be no common design principles.
The new HSE guidance (HSG 258) states that there are only three types of LEV hood.

## Slide 9
Capturing (Capture)
The three basic types of LEV hood
Enclosing (Contain and separate)
Receiving (Receive, contain & empty)
Source: HSE
Notes: <number>
Enclosures – process takes place inside the hood. The hood needs to contain the airborne contaminant and keep it separate from the worker
Receptor – process takes place outside of the hood, but the process generates directional air movement towards the hood. The hood needs to receive the contaminated laden air and to ensure it works effectively it needs to empty at lease as quick as it is being filled.
Capturing – process takes place outside the hood. The hood has to generate sufficient air movement towards the hood at the far side of the source. Effectively, the hood has to reach out and capture the contaminant laden air.
Most LEV hoods fall into one of the above categories, but sometimes hoods do operate in ‘mixed mode’

## Slide 10
Partial, large
Room
LEV hood classification expanded
Receiving
Capturing
Hot
Partial, small
Full
Enclosures
Source: HSE
Notes: <number>
Hemeon refers to three different types of hood; exterior (which is equivalent to capturing), enclosing and Canopy or receiving hood
Enclosures – Can be subdivide - full, partial (large), partial (small), room
Receiving – Process moves in one direction. classic receiving hood is the canopy hood above a hot process
In practice the guidance will use the classification to outline key design factors for each type of hood and common errors but also will refer to and use the more familiar terms where appropriate e.g. enclosure, partial enclosure and canopy hood

## Slide 11
LEV system design, the most critical element is the hood
Main reasons why systems fail to protect:
Incorrect type of hood is chosen (and could never provide sufficient protection)
The airborne contaminant isn’t contained or captured.
LEV hood design doesn’t match the process and source(s)
Insufficient airflow (various reasons).
Source: HSE
Notes: <number>
Most LEV systems fail to control exposure because the airborne contaminant never enters or doesn’t stay in the hood
Various reasons include: poor maintenance leading to hood damage, duct and/or air-cleaner blockage, holes in ductwork, system goes out-of-balance (various reasons including opening and closing of dampers), fan performance degrades (e.g. damage to blades or housing, drive-belt breakage or slippage)
Insufficient airflow – degrades with time. Often a system will make the same noise as the day it was installed, but the flow rate could be dramatically lower.

## Slide 12
Process takes place outside hood, hood-induced airflow has to “capture” contaminant-laden air
(adapted from Hemeon’s Plant and Process Ventilation)
Side-draught captor hood
Capturing Hoods
Source: HSE
Notes: <number>
Capture hoods often ‘shoe horned’ into a process as an afterthought. Therefore, placed where it can be fitted rather that where it should be placed.

## Slide 13
Capturing Hoods
(adapted from Hemeon’s Plant and Process Ventilation)
Hood has to generate sufficient airflow at and around the source to ‘capture’ and draw in the contaminant-laden air
The process, source and contaminant cloud are outside the hood
Source: HSE
Notes: <number>
All capture hoods work on the same principles – regardless of size

## Slide 14
Capturing Hoods – interrelated properties
Capture velocity, distance and zone (new(ish))
Process induced air movement and draughts
Airflow, velocity contours and flanges
Capture ‘bubbles’ (new)
Capture curve (new)
Capture zone and Working Zone (new).
Source: HSE
Notes: <number>
Some of the above are new concepts or new ways of expressing hood properties.

## Slide 15
Air velocity required
at this point to
“capture” vapour-laden air ~0.5 metres per second (m/s)
Capture of vapour-laden air: evaporation
Source: HSE
Notes: <number>
Quiet source – e.g. evaporation of solvent. Relatively low capture velocity required

## Slide 16
Capture of vapour-laden air: drum filling
Air velocity required
at this point to
“capture” vapour-laden air ~2.5 metres per second (m/s)
Source: HSE
Notes: <number>
More energetic process – hence larger capture velocity required

## Slide 17: Receptor Hoods
Source: HSE

## Slide 18: Enclosing Hood
Source: HSE

## Slide 19: Types of LEV used for various processes
Industrial process | Nature of hazardous substance | Types of LEV
Welding | Welding fume: fine particulate with some natural buoyancy | Capture hood positioned close to the welding activity; or Tip extraction fitted to the end of the welding gun
Paint spraying | Mist and solvent vapours released in controlled direction with velocity | Walk in paint spray booth Down flow booth
Polishing | Metal and polishing dust released in controlled direction with high velocity | Receptor hood and enclosure around the polishing wheel
Shot blasting | Steel shot and metal dust from components released at high velocity in variable direction | Fully enclosed glove box type cabinet with airflow managed to compensate for compressed air input and shot recycling system
Hand held orbital Sander | Wood dust released in variable directions | Extraction integrated into the sander disc
Paint curing Ovens | Hot air and curing vapours with strong thermal buoyancy | Extract/vent from top of oven combined with a receptor hood over the doorway
Laboratory analysis | Acid and solvent vapours released with low velocity and little direction | Partial enclosure and extraction within a fume cupboard
Source: HSE

## Slide 20
Capture Zone / Capture Bubble
Notes: <number>

## Slide 21
Capture bubble
Movable capturing hood – capture ‘bubble’
Source: HSE
Notes: <number>
Can think of the capture zone as a bubble.

## Slide 22
Capture ‘bubble’ varies in size
Source: HSE
Notes: <number>
Capture bubble will vary in size depending upon air movement in the room – degree of draughts in the room.

## Slide 23
Capturing hood capture ‘bubble’
Source: HSE
Notes: <number>
Demonstration of the change in size of a capture bubble.
Worker soldering in front of a capturing hood – okay at one position, but as she moves away capture falls – small ‘capture bubble’

## Slide 24
Capture zone must encompass working zone
Capture zone
Working zone
Source: HSE
Notes: <number>
Shows capture zone and working zone. Capture zone must encompass the working zone. if it does not the hood is not effective. Hood has failed to control exposure.

## Slide 25: Ductwork
Ductwork carries the extracted air and the contaminant from the inlet to the air cleaning device.
  Velocity Important
  Should be sufficiently strong
  Well supported and capable of withstanding normal wear and tear
  The number of changes of directions should be kept to a minimum
  Should be made smoothly
  Access to ducting may be required.

## Slide 26: Duct Velocity
Type of contaminant | Duct velocity (m sec-1)
Gases (non‑condensing) | No minimum limit
Vapours, smoke, fume | 10
Light/medium density dust (e.g. sawdust, plastic dust) | 15
Average industrial dusts (e.g. grinding dust, wood shavings, asbestos, silica) | 20
Heavy dusts, (e.g. lead, metal turnings and dusts which are damp or that tend to agglomerate) | 25
Source: HSE

## Slide 27: Air Cleaners - Filters
Source: Adrian Hirst

## Slide 28: Air Cleaners - Cyclones
Source: Adrian Hirst

## Slide 29: Air Cleaners - Wet Cyclone & Induct Spray
Source: Adrian Hirst

## Slide 30: Air Movers - Fans
Source: US EPA
Axial
Centrifugal

## Slide 31: Discharge to Atmosphere
Source: HSE

## Slide 32: Maintenance, Examination and Testing of Ventilation Systems
In order to function correctly it must be in good working order.
  Legal requirements
  Regular Maintenance
  Thorough Examination and Testing.